INSPECTION AND TEST PLAN (ITP)

| PROJECT INFORMATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project Name | Kalgoorlie Airport Hotel (CDI 6425) | Location | 10 Gatacre Drive, Somerville WA 6430 | Scope Overview | Earthworks - fill, excavation to formation, detailed excavation for footings & pits, fill & compaction (Building 1, Buildings 2 & 3, External Works) |
| Subcontractor | Kooboolong Services Pty Ltd | Trade Package | Earthworks |  |
| ITP Ref. | 6425-KBS-ITP-001 | Revision | B | Date | 23/09/2026 |
| Lot/Location | Building 1 / Buildings 2 & 3 / External Works |  |  |  |  |

| CDI GROUP APPROVAL |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CDI Approval | Name |  | Position | ☐ PM | ☐ SM | ☐ Other (specify) | Signature |  | Date |
| Initial |  |  |  |  |  |

| REFERENCE DOCUMENTATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project Specifications and Drawings |  | Referenced Standards |  | Associated ITR Inspection Numbers |  |
| Specification Number | Specification Title | Standard Reference | Standard Title | ITR Reference | ITR Title |
| Spec REP_GEO | Geotechnical Report - founding, fill specification, compaction & testing | AS 3798 | Guidelines on earthworks for commercial and residential developments | 6425-KBS-ITR-001 | Earthworks Lot Record (clearing & strip, proof roll, fill source, founding) |
| DWG No: C-003 | Bulk Earthworks Plan | AS 1289 (1289.5, 5.4.1, 5.7.1, 5.8.1) | Methods of testing soils for engineering purposes - compaction & density | 6425-KBS-ITR-001A | Earthworks Test Register (compaction & CBR tests) |
| DWG No: C-001 / C-002 | Civil General Arrangement / Drainage & Grading Plan | AS 1726 | Geotechnical site investigations - soil classification | 6425-KBS-ITR-001B | Waste / Spoil Disposal Docket Register |
| DWG No: C-010 / C-011 | Civil Details Sheets 1 & 2 | AS 1141 | Methods for sampling and testing aggregates | 6425-KBS-ITP-002 | Concrete on Ground ITP |
| DWG No: S090 / S095 / S100 | Excavation & Batter Plan, Footing Plans - Buildings 2 & 3 |  |  |  |  |
| DWG No: S100_B1 | Ground Floor & Footing Plan - Building 1 |  |  |  |  |
| DWG No: S001_B1 / S001 / S002 | Structural General Notes - founding requirements |  |  |  |  |
| Site Logistics Plan / Services Clearance | CDI logistics plan; written underground services clearance per area |  |  |  |  |

Type of Inspection:  H = HOLD (work shall not proceed past this point without verified acceptance)   W = WITNESS (nominee notified and invited; work may proceed)   R = REVIEW (verification by documentary evidence)

| No. | Description of required activity | Governing specification or standard | Acceptance Criteria | Record of compliance / completion | Kooboolong | CDI | Engineer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |  |
| 1. | - Review SOW, SWMS, drawings, geotechnical report and specification | - LOI 6425-COM-SC-LOI-002 Att. 2 - REP_GEO - CSP | - Contract scope, exclusions (rock / hard digging, latent conditions, services location, potholing, retaining walls, swales, dewatering, sediment control) and clarifications confirmed in writing - Current IFC revision of civil and structural drawings confirmed on Procore - Fill material specification, layer thickness, compaction standard, moisture range and test frequency extracted from geotechnical report and CSP - Founding requirements (bearing, material, inspection) extracted from structural general notes | - Prior to works commencing - Document review record | H, R | H, R |  |
| 2. | - Survey control and set-out | - CDI survey control - DWG No: C-001 / C-003 - FS-ID-001 | - Grid lines, datum and control marks received from CDI in writing and checked against the feature survey - Extent of clearing, strip, cut, fill, batters and building platforms set out; batter and platform RLs taken from IFC drawings - Pre-start dated photo record of the whole site, adjoining surfaces and access roads | - Set-out record - Photos | W | W |  |
| 3. | - Underground services clearance | - CDI services information - Site Logistics Plan | - Written clearance from CDI for each area before any ground is broken; location, potholing and protection of services is excluded from KBS scope - Known services marked on the ground; exclusion zones and hand-dig / spotter requirements briefed at pre-start - Any unidentified service: stop, isolate, notify CDI immediately | - CDI written clearance - Pre-start record | H | H |  |
| 4. | - Environmental controls and existing trees | - CSP - AS 4970 | - Trees to be retained identified and protected by others; KBS plant kept outside protection zones - Dust suppression: water cart available during KBS working hours; fill point confirmed by CDI | - Photos - Pre-start record | R | W |  |
| STRIP & BULK EARTHWORKS |  |  |  |  |  |  |  |
| 5. | - Bulk excavation to formation / cut | - DWG No: C-003 - DWG No: S090 - REP_GEO | - Cut to formation levels and batters shown - Formation within tolerance before proof roll - Excavated material stockpiled for reuse only where the geotech report allows; surplus removed with dockets - Rock or hard digging is excluded - photograph, measure and notify CDI in writing the same day before proceeding | - Level survey - Photos - Notice (if rock) | W | W |  |
| 6. | - Subgrade / formation proof roll | - AS 3798 cl. 6 - REP_GEO - CSP | - Exposed subgrade proof rolled with roller - No visible deflection, heave or rutting; soft or wet areas excavated and replaced with approved fill to Engineer direction - Subgrade moisture conditioned and compacted before fill - HOLD POINT - no fill placed on unapproved subgrade | - Earthworks Lot Record 6425-KBS-ITR-001 (HP1) - Geotech sign-off - Photos | H | W | H |
| FILL & COMPACTION |  |  |  |  |  |  |  |
| 7. | - Fill material source approval | - REP_GEO - CSP - AS 1289 / AS 1726 | - Imported engineered fill from nominated source tested before delivery: grading, plasticity, CBR, free of organics, contaminants and oversize - Site fill only where the geotechnical report permits and tested to the same standard - Source and test results submitted to CDI / geotech for approval before bulk delivery; no change of source without re-approval | - Earthworks Lot Record 6425-KBS-ITR-001 (Q11) - Lab reports - Delivery dockets | H | R | H |
| 8. | - Fill placement | - AS 3798 cl. 5 - REP_GEO - CSP | - Fill placed in horizontal layers not exceeding typically 200-300 mm loose thickness, moisture conditioned to spec. - Fill over service trenches (excavated and initially backfilled by others) only after as-constructed received and initial backfill inspected - Fill kept free of ponding; rain-affected layers scarified, dried and recompacted | - Layer record - Test Register 6425-KBS-ITR-001A | W | W |  |
| 9. | - Compaction testing | - AS 1289.5.4.1 / 5.7.1 / 5.8.1 - AS 3798 Table 8.1 - REP_GEO / CSP | - NATA-accredited field density testing at frequency - typically 1 test per 500 m2 per layer or per 250 m3, minimum 2 per layer - Acceptance: typically minimum 95% standard MDD general fill; 98% under footings / slabs; 100% within top 300 mm of pavement subgrade - Failed tests: layer reworked and retested; retest recorded beneath the failed test on the register, no layer covered until passed - Results to CDI within 2 business days of receipt | - NATA test reports - Test Register 6425-KBS-ITR-001A | H | R | H |
| 10. | - Final formation acceptance | - DWG No: C-003 - REP_GEO - AS 3798 | - Finished formation and pavement subgrade levels surveyed: within tolerance - Final proof roll witnessed; surface trimmed and lightly compacted; free of loose material - Platform protected from traffic and weather until following trade takes over; damage before handover made good by KBS - HOLD POINT - handover to concrete works (ITP-002) and to others | - Level survey - Proof Roll Record - Earthworks Lot Record 6425-KBS-ITR-001 (HP3) | H | W | H |
| DETAILED EXCAVATION |  |  |  |  |  |  |  |
| 11. | - Detailed excavation - footings, pits, lift pit, sumps | - DWG No: S100_B1 / S095 / S100 - DWG No: S090 - REP_GEO | - Excavated to line, level and dimension - Sides stable or battered per SWMS; excavations left open protected with barriers and edge protection, never left open overnight unprotected - Base clean, dry and free of loose material; over-excavation made good with approved fill or concrete per Engineer direction - Dewatering after detailed excavation or rain is excluded - notify CDI | - Earthworks Lot Record 6425-KBS-ITR-001 (section D) - Photos | W | W |  |
| 12. | - Founding inspection | - Structural general notes - REP_GEO | - Founding material at every pad, strip and pit inspected by CDI engineer and confirmed as the material and bearing - Unsuitable founding: stop, notify CDI in writing, Engineer direction obtained (deepen, replace with engineered fill or concrete) - HOLD POINT - no blinding, membrane, formwork or reinforcement until released; 24 h notice given to CDI and Engineer | - Earthworks Lot Record 6425-KBS-ITR-001 (HP2) - Engineer sign-off - Photos | H | W | H |
| ACCESS TRACKS, CRANE PADS & SITE |  |  |  |  |  |  |  |
| 13. | - Stockpiles, spoil and waste | - CSP - CDI HSEQ plan - Waste tracking requirements | - Stockpiles in locations agreed with CDI, kept tidy, not against structures or over services - All spoil and waste removed to a licensed facility; every docket retained and logged (classification per facility requirements) - Contaminated or unexpected material: stop, isolate, notify CDI - disposal by direction | - Disposal Docket Register 6425-KBS-ITR-001B | R | R |  |
| COMPLETION |  |  |  |  |  |  |  |
| 14. | - Earthworks certification and handover | - AS 3798 - REP_GEO | - Geotechnical engineer's compliance / certification report covering subgrade approvals, fill source, layer records and all test results - All test registers, proof roll and founding records, disposal dockets and NCRs closed and issued to CDI - Site left tidy; tracks reinstated; this ITP signed and issued | - Geotech certification report - Signed ITP - Registers | H | H | R |

ITP Comments and Notes:

Works completed and testing completed in line with this ITP except as noted above.

| Reviewed and accepted by: | Earthworks - Kooboolong Services | CDI Group |
| --- | --- | --- |
| Name: | Mitchell van Zyl |  |
| Position/Title: | Project Manager |  |
| Date: |  |  |
| Signature: |  |  |